## NMISA-HVAC-
NMISA-HVAC-
NMISA BUILDING 4 - HVAC INSTALLATION
SECTION | BILL | PAGE NO | ITEM NO | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 1 | 1 |  | Bill 1: Preliminary and General | H1 | 0
1 | 1 | 1 | 1 | Technical Submissions | SUM | 1
1 | 1 | 1 | 2 | Allow fully for compliance with the Conditions of Contract as is applicable to the Main Contract. | SUM | 1
1 | 1 | 1 | 3 | Allow for compliance with general matters relating to these specifications. | SUM | 1
1 | 1 | 1 | 4 | Allow for compliance with Occupational Health & Safety Act and Regulations and other statutory requirements. | SUM | 1
1 | 1 | 1 | 5 | Operating and maintenance manuals including as-built drawings. 3 sets. | SUM | 1
1 | 1 | 1 | 6 | Allow for the guarantee of the complete installation for a period of 12 months. | SUM | 1
1 | 1 | 1 | 7 | Allow for the full maintenance of the installation for a period of 12 months. | No | 1
1 | 1 | 1 | 8 | Allow for the provision of electrical certificate of compliance for all | SUM | 1
1 | 1 | 1 | 9 | Mechanical related electrical work. | SUM | 1
1 | 1 | 1 | 10 | Site Establishment | SUM | 1
1 | 1 | 1 | 11 | Rigging of new equipment | SUM | 1
1 | 1 | 1 | 12 | Protection Against Damage | SUM | 1
1 | 1 | 1 | 13 | Transport | SUM | 1
1 | 1 |  |  |  |  | 0
1 | 2 | 2 |  | Bill 2: Chiller Plant & AHUs | H1 | 0
1 | 2 | 2 |  | Supply, Deliver, Install and commision the following Air cooled, energy efficient, 122kW cooling capacity (York YMPA 130 or similar approved) Chiller, complete with inverter compressors, sound attenuation, soft start, controls and low noise fuetures, Tracer summit, temprature in/out 12/7 degrees C, mounted on I-beams and Hail gaurds for protection as per Specifications | H3 | 0
1 | 2 | 2 | 1 | CH1 | No | 1
1 | 2 | 2 | 2 | Commissioning by Supplier | SUM | 1
1 | 2 | 2 | 3 | Anti Vibration Mountings | SUM | 1
1 | 2 | 2 |  | Supply, Deliver, Install and commision the Primary Chilled Water Circulating pumps 1 & 2 constant speed, fluid water c/w, frame, anti vibration, mounts and stainless steel drip tray 5.5 l/s at 220 kPA head pressure, high pressure seals One (1) operational & one (1) standby. | H3 | 0
1 | 2 | 2 | 4 | P1 & P2 | No | 2
1 | 2 | 2 |  | Supply, Deliver, Install and commision the following air handling units c/w brackets, heater banks, filters, EC fans, controls to complete the AHU installation, | H3 | 0
1 | 2 | 2 | 5 | AHU01 (TC - 48,9kW) | No | 1
1 | 2 | 2 | 6 | AHU 2 (TC - 60kW) | No | 1
1 | 2 | 2 | 7 | AHU 3 (TC - 17kW) | No | 1
1 | 2 | 2 | 8 | Electronic Controllers with all sensors, relays, selector switches and warning lights | No | 3
1 | 2 | 3 | 9 | Canvas Collars and transformation pieces to connect to supply and return ducts | No | 6
1 | 2 | 3 | 10 | Anti Vibration Mountings | SUM | 3
1 | 2 | 3 | 11 | I-beam base frame | SUM | 2
1 | 2 | 3 | 12 | AHU03 Hanger fixing to slab | SUM | 1
1 | 2 | 3 |  | Supply, Deliver, Install and commision the following Carel (or similar approved) Humidifiers complete with intergrated controls to connect to main Johnsons HVAC controls and in duct diffusers | H3 | 0
1 | 2 | 3 | 13 | HM1 (Carel UE025) | No | 2
1 | 2 | 3 | 14 | HM2 (Carel UE005) | No | 1
1 | 2 | 3 |  | Supply, Deliver, Install and commision complete automatic water treatment system that is integrated with the HVAC main control system for management alerts etc. | H3 | 0
1 | 2 | 3 | 15 | Water treatment system | SUM | 1
1 | 2 | 3 |  | Miscellaneous | H3 | 0
1 | 2 | 3 |  | Any items not specified mentioned and not covered in the items above - specify | H4 | 0
1 | 2 | 3 | 16 | ….......................................... | SUM | 0
1 | 2 | 3 | 17 | ….......................................... | SUM | 0
1 | 2 | 3 | 18 | ….......................................... | SUM | 0
1 | 2 |  |  |  |  | 0
1 | 3 | 5 |  | Bill 3: Controls | H1 | 0
1 | 3 | 5 |  | Supply, deliver, install and comission complete as per specifications: | H3 | 0
1 | 3 | 5 | 1 | Weather proof powder coated metal DB boards to house Electronic Controller with all sensors, relays, selector switches and pilot lights for CHW pumps switch over and pressure control.All breakers and isolators to be included in this item. DB to have filtered forced ventilation to protect controls. | SUM | 1
1 | 3 | 5 | 2 | Weather proof powder coated metal DB boards to house Electronic Controller with all sensors, relays, selector switches and pilot lights for AHUs & Humidifier, switch over and pressure/airflow controls.All breakers and isolators to be included in this item. DB to have filtered forced ventilation to protect controls. | SUM | 3
1 | 3 | 5 | 3 | T89 wall thermostat type Room Controllers or similar approved c/w duel room temprature and humidity sensors for each lab and cabeling | No | 30
1 | 3 | 5 |  | Supply, deliver and install HVAC Controls System with the following Components. | H3 | 0
1 | 3 | 5 | 4 | HVAC Intergrated into DB Workstation/front end with modem/sms notifications | SUM | 1
1 | 3 | 5 | 5 | HVAC Software Graphics & Engineering | SUM | 1
1 | 3 | 5 | 6 | HVAC Controls Programming | SUM | 1
1 | 3 | 5 | 7 | AHU Controller integration with SAG Controls. (Hardware and software) | SUM | 1
1 | 3 | 5 | 8 | Chiller integration with HVAC Central main controller (Hardware and Software) | SUM | 1
1 | 3 | 6 | 9 | Fresh air integration with HVAC Central main controller (Hardware and Software) | SUM | 3
1 | 3 | 6 | 10 | AHUs integration with HVAC Central main controller (Hardware and Software) | SUM | 3
1 | 3 | 6 | 11 | Humidifier integration with HVAC Central main controller (Hardware and Software) | SUM | 3
1 | 3 | 6 | 12 | Commissioning of all HVAC Controls, hardware and software by supplier | SUM | 1
1 | 3 | 6 | 13 | Supply, deliver and install control wiring between SAG/controllers/sensors/controllers complete. Wiring to be fixed to ducting with light duty cable trays. | SUM | 1
1 | 3 | 6 |  | Miscellaneous | H3 | 0
1 | 3 | 6 |  | Any items not specified mentioned and not covered in the items above - specify | H4 | 0
1 | 3 | 6 | 14 | ….......................................... | SUM | 0
1 | 3 | 6 | 15 | ….......................................... | SUM | 0
1 | 3 | 6 | 16 | ….......................................... | SUM | 0
1 | 3 |  |  |  |  | 0
1 | 4 | 8 |  | Bill 4: Chilled Water Piping | H1 | 0
1 | 4 | 8 |  | Supply, deliver, install and commision c/w welded, support wire mesh tray/rack fixed to structure and pipework lifted into possition joints weld and flanges where required, bolts nuts, etc, c/w all necessary fittings/assembly for complete installation as per specification: | H3 | 0
1 | 4 | 8 |  | PPR PN16 Pipe | H4 | 0
1 | 4 | 8 | 1 | Ø65 | m | 34
1 | 4 | 8 | 2 | Ø50 | m | 14
1 | 4 | 8 | 3 | Ø40 | m | 25
1 | 4 | 8 | 4 | Ø32 | m | 60
1 | 4 | 8 | 5 | Ø25 | m | 35
1 | 4 | 8 |  | Equal tee | H4 | 0
1 | 4 | 8 | 6 | Ø65 | No | 24
1 | 4 | 8 | 7 | Ø50 | No | 12
1 | 4 | 8 | 8 | Ø40 | No | 14
1 | 4 | 8 | 9 | Ø32 | No | 6
1 | 4 | 8 | 10 | Ø25 | No | 12
1 | 4 | 8 |  | Bend (90°) | H4 | 0
1 | 4 | 8 | 11 | Ø65 | No | 20
1 | 4 | 8 | 12 | Ø50 | No | 16
1 | 4 | 9 | 13 | Ø40 | No | 16
1 | 4 | 9 | 14 | Ø32 | No | 20
1 | 4 | 9 | 15 | Ø25 | No | 20
1 | 4 | 9 |  | Concentric Reducers | H4 | 0
1 | 4 | 9 | 16 | Ø65 | No | 26
1 | 4 | 9 | 17 | Ø50 | No | 14
1 | 4 | 9 | 18 | Ø40 | No | 14
1 | 4 | 9 | 19 | Ø32 | No | 6
1 | 4 | 9 | 20 | Ø25 | No | 14
1 | 4 | 9 |  | Coupling | H4 | 0
1 | 4 | 9 | 21 | Ø65 | No | 22
1 | 4 | 9 | 22 | Ø50 | No | 8
1 | 4 | 9 | 23 | Ø40 | No | 10
1 | 4 | 9 | 24 | Ø32 | No | 32
1 | 4 | 9 | 25 | Ø25 | No | 15
1 | 4 | 9 |  | Supply delivery and install and commision the following c/w all necessary fittings /assembly for the complete installation: | H3 | 0
1 | 4 | 9 |  | Flexible Connections c/w Installed, including matching flanges where required, bolts, nuts, ens | H4 | 0
1 | 4 | 9 | 26 | Ø65 | No | 4
1 | 4 | 9 | 27 | Ø50 | No | 2
1 | 4 | 10 | 28 | Ø40 | No | 2
1 | 4 | 10 | 29 | Ø25 | No | 6
1 | 4 | 10 |  | Strainers: c/w Installed, including matching flanges where required, bolts, nuts, etc | H3 | 0
1 | 4 | 10 | 30 | Ø65 | No | 2
1 | 4 | 10 | 31 | Ø25 | No | 2
1 | 4 | 10 |  | Butterfly Valves: c/w Installed, including matching flanges where required, bolts, nuts, etc | H3 | 0
1 | 4 | 10 | 32 | Ø65 | No | 6
1 | 4 | 10 |  | Ball Valves: | H3 | 0
1 | 4 | 10 | 33 | Ø50 | No | 8
1 | 4 | 10 | 34 | Ø40 | No | 10
1 | 4 | 10 | 35 | Ø25 | No | 24
1 | 4 | 10 |  | Miscellaneous Equipment | H3 | 0
1 | 4 | 10 | 36 | Dial type glycerine-filled pressure gauges (c/w cock+syphon tube) | No | 12
1 | 4 | 10 | 37 | Flow switch | No | 4
1 | 4 | 10 | 38 | Pipe thermometer and well | No | 16
1 | 4 | 10 | 39 | Air vent valve (Automatic) | No | 12
1 | 4 | 10 | 40 | Pressure reducing/regulating valve Ø25 | No | 2
1 | 4 | 10 | 41 | Binder point | No | 14
1 | 4 | 10 | 42 | 3L Expantion tank | No | 1
1 | 4 | 11 | 43 | Tico pads | SUM | 1
1 | 4 | 11 |  | Balancing (STA-T) Valves: c/w Installed, including matching flanges where required, bolts, nuts, etc | H3 | 0
1 | 4 | 11 | 44 | Ø50 | No | 1
1 | 4 | 11 | 45 | Ø40 | No | 1
1 | 4 | 11 | 46 | Ø25 | No | 4
1 | 4 | 11 |  | Non-Return (check) Valves: c/w Installed, including matching flanges where required, bolts, nuts, etc | H3 | 0
1 | 4 | 11 | 47 | Ø65 | No | 2
1 | 4 | 11 | 48 | Ø25 | No | 4
1 | 4 | 11 |  | Motorised valve c/w Installed, including matching flanges where required, bolts, nuts, ens, 24V | H3 | 0
1 | 4 | 11 | 49 | Ø50 | No | 1
1 | 4 | 11 | 50 | Ø40 | No | 1
1 | 4 | 11 | 51 | Ø25 | No | 2
1 | 4 | 11 |  | Screw Flanges (AHU and Chiller) where required, bolts, nuts, ens | H3 | 0
1 | 4 | 11 | 52 | Ø65 | No | 2
1 | 4 | 11 | 53 | Ø50 | No | 2
1 | 4 | 11 | 54 | Ø40 | No | 2
1 | 4 | 11 | 55 | Ø25 | No | 4
1 | 4 | 11 | 56 | Dosing pot arrangement. | No | 1
1 | 4 | 12 |  | Chilled Water Insulation K-Flex Elastomeric Foam Insulation | H3 | 0
1 | 4 | 12 | 57 | Ø65 | m | 34
1 | 4 | 12 | 58 | Ø50 | m | 14
1 | 4 | 12 | 59 | Ø40 | m | 25
1 | 4 | 12 | 60 | Ø32 | m | 60
1 | 4 | 12 | 61 | Ø25 | m | 35
1 | 4 | 12 |  | Fittings | H3 | 0
1 | 4 | 12 | 62 | K-Flex Elastomeric Foam Isulation for all above fittings for the complete installation | SUM | 1
1 | 4 | 12 | 63 | All extrnal pipe to be galv gladed for the complete installation | SUM | 1
1 | 4 | 12 |  | Miscellaneous | H3 | 0
1 | 4 | 12 |  | Any items not specified mentioned and not covered in the items above - specify | H4 | 0
1 | 4 | 12 | 64 | ….......................................... | SUM | 0
1 | 4 | 12 | 65 | ….......................................... | SUM | 0
1 | 4 | 12 | 66 | ….......................................... | SUM | 0
1 | 4 |  |  |  |  | 0
1 | 5 | 14 |  | Bill 5: Ducting | H1 | 0
1 | 5 | 14 |  | Ground Floor | H2 | 0
1 | 5 | 14 |  | Air Distribution System | H3 | 0
1 | 5 | 14 |  | Supply, deliver, install and commision c/w supporting hangers, seal, etc for complete installation as per specification: | H4 | 0
1 | 5 | 14 | 1 | A1 - Straight duct 850x550 | m | 140
1 | 5 | 14 | 2 | A2 - Bend90 850x550 | No | 10
1 | 5 | 14 | 3 | A3 - Equal taper 850x550 to 550x450 | No | 2
1 | 5 | 14 | 4 | A4 - Straight duct 550x450 | m | 93
1 | 5 | 14 | 5 | A5 - Straight duct 400x400 | m | 11
1 | 5 | 14 | 6 | A10 - Bend90 400x400 | No | 1
1 | 5 | 14 |  | (Internal Insulated Ducting 25mm Sonic) | H4 | 0
1 | 5 | 14 | 7 | A6 - Straight duct 850x450 c/w 25mm sonic | m | 146
1 | 5 | 14 | 8 | A7 - Bend 90° 850 450 c/w 25mm Sonic | No | 10
1 | 5 | 14 | 9 | A8 - Equal Taper c/w 25mm Sonic 850x550 to 550x450 | No | 2
1 | 5 | 14 | 10 | A9 - Straight Duct c/w 25mm Sonic 550x450 | No | 94
1 | 5 | 14 | 11 | C1 - Endcap 550x450 | No | 2
1 | 5 | 14 | 12 | C2- Spigot 400x400 | No | 2
1 | 5 | 14 | 13 | C3 - Endcap 550x450 | No | 2
1 | 5 | 15 | 14 | C4 - Plenum 550x300 | No | 24
1 | 5 | 15 | 15 | FD1 - Fire damper 850x450 | No | 1
1 | 5 | 15 | 16 | FD2 - Fire damper 850x550 | No | 1
1 | 5 | 15 | 17 | HB 1 - Heater Bank 6kW c/w matching OBD and actuator (3 step) 400x400 (Belimo type Actuators) | No | 2
1 | 5 | 15 | 18 | RA 1 - Return Air Grille c/w lockable quadrant 500x250 | No | 24
1 | 5 | 15 | 19 | SAG 1 - Side Wall Variable Volume Diffuser c/w Matching OBD, actuator and Heater bank (2.5kW) 500x250 (Belimo type Actuators) | No | 24
1 | 5 | 15 | 20 | WL 1 -Hinged Weather Louvre c/w matching OBD 400x400 | No | 2
1 | 5 | 15 |  | Stripping | H3 | 0
1 | 5 | 15 | 21 | Strip and remove from site existing ducting, dampers, fittings, grilles, etc, | SUM | 1
1 | 5 | 15 |  | First Floor Ducting | H2 | 0
1 | 5 | 15 |  | Air Distribution System | H3 | 0
1 | 5 | 15 |  | Supply, deliver, install and commision c/w supporting hangers, seal, etc for complete installation as per specification: | H4 | 0
1 | 5 | 15 | 22 | A1 - Straight duct 650x400 | m | 2
1 | 5 | 15 | 23 | A2 - Straight duct 300x300 | m | 10
1 | 5 | 15 | 24 | A3 - Bend90 300x300 | No | 6
1 | 5 | 15 | 25 | A4 - Straight duct 400x400 | m | 15
1 | 5 | 15 | 26 | A5 - Straight duct 400x400 | m | 4
1 | 5 | 16 |  | (Internal Insulated Ducting 25mm Sonic) | H4 | 0
1 | 5 | 16 | 27 | A5 - Straight duct 650x450 c/w sonic 25mm | m | 4
1 | 5 | 16 | 28 | A6 - Straight duct 300x300 c/w sonic 25mm | m | 15
1 | 5 | 16 | 29 | A7 - Bend 90 c/w sonic 25mm | No | 4
1 | 5 | 16 | 30 | A8 - Straight duct 400x400 c/w sonic 25mm | m | 13
1 | 5 | 16 | 31 | A9 - Straight duct 150x150 c/w sonic 25mm | m | 6
1 | 5 | 16 | 32 | C1 - Endcap 650x400 | No | 1
1 | 5 | 16 | 33 | C2 - Spigot 300x300 | No | 3
1 | 5 | 16 | 34 | C3 - Endcap 300x300 | No | 2
1 | 5 | 16 | 35 | C4 - Spigot 400x400 | No | 3
1 | 5 | 16 | 36 | C5 - Endcap 400x400 | No | 3
1 | 5 | 16 | 37 | C6 - Endcap 650x400 | No | 1
1 | 5 | 16 | 38 | C7 - Spigot 150x150 | No | 1
1 | 5 | 16 | 39 | C8 - Endcap 150x150 | No | 1
1 | 5 | 16 | 40 | C9 - Plenum 550x300 | No | 7
1 | 5 | 16 | 41 | HB1 - Heater Bank 2.5kW c/w matching OBD and actuator (3 step) (Belimo type Actuators) | No | 1
1 | 5 | 16 | 42 | RA 1 - Return Air Grille c/w lockable quadrant 500x250 | No | 8
1 | 5 | 16 | 43 | SAG 1 - Side Wall Variable Volume Diffuser c/w Matching OBD, actuator and Heater bank (2.5kW) 500x250 (Belimo type Actuators) | No | 8
1 | 5 | 17 | 44 | SAG 2 - Side Wall Variable Volume Diffuser c/w Matching OBD, actuator and Heater bank (2.5kW) 300x150 (Belimo type Actuators) | No | 1
1 | 5 | 17 | 45 | WL 1 - Hinged Weather Louvre c/w matching OBD 300x300 | No | 1
1 | 5 | 17 |  | Stripping | H4 | 0
1 | 5 | 17 | 46 | Strip and remove from site existing ducting, dampers, fittings, grilles, etc, | SUM | 1
1 | 5 | 17 | 47 | Balancing of the entire ducting system | SUM | 1
1 | 5 | 17 |  | Fire Damper with spring return actuator c/w limit switch integration to HVAC main controls to switch off | H4 | 0
1 | 5 | 17 | 48 | 850x450 | No | 4
1 | 5 | 17 | 49 | 850x550 | No | 4
1 | 5 | 17 |  | Miscellaneous | H3 | 0
1 | 5 | 17 |  | Any items not specified mentioned and not covered in the items above - specify | H4 | 0
1 | 5 | 17 | 50 | ….......................................... | SUM | 0
1 | 5 | 17 | 51 | ….......................................... | SUM | 0
1 | 5 | 17 | 52 | ….......................................... | SUM | 0
1 | 5 |  |  |  |  | 0
1 | 6 | 19 |  | Bill 6: Builders Work & Existing Equipment | H1 | 0
1 | 6 | 19 | 1 | Removal of existing HVAC equipment in room 050 with the condenser unit and as per specification | SUM | 1
1 | 6 | 19 | 2 | Making of openings for ducting as per project drawings and making good | SUM | 1
1 | 6 | 19 | 3 | Making of openings for louvres as per project drawings with sleeves and making good | SUM | 1
1 | 6 | 19 | 4 | Allowing for painting of plantroom walls, floor and piping bands for the complete finish as per specifications | SUM | 1
1 | 6 | 19 |  | Miscellaneous | H3 | 0
1 | 6 | 19 |  | Any items not specified mentioned and not covered in the items above - specify | H4 | 0
1 | 6 | 19 | 5 | ….......................................... | SUM | 0
1 | 6 | 19 | 6 | ….......................................... | SUM | 0
1 | 6 | 19 | 7 | ….......................................... | SUM | 0
1 | 6 |  |  |  |  | 0
1 | 7 | 20 |  | BILL No.7 | H1 | 0
1 | 7 | 20 |  | WORK GROUP NUMBER 160 | H2 | 0
1 | 7 | 20 |  | EXISTING INSTALLATION | H4 | 0
1 | 7 | 20 |  | Allow of removing the existing electrical installation infrastructure: | H4 | 0
1 | 7 | 20 | 1 | CSIR Building (Electrical Aircon Section Only) | Item | 1
1 | 7 | 20 |  | LT CABLES | H3 | 0
1 | 7 | 20 |  | 600/1000 volt PVC/PVC/SWA/PVC copper cable pulled through sleeves, laid in trenches. (trenching and backfilling measured elsewhere) | H4 | 0
1 | 7 | 20 | 2 | 240mm² x 4-core ECC | m | 30
1 | 7 | 20 | 3 | 50mm² x 4-core ECC | m | 35
1 | 7 | 20 | 4 | 16mm² x 4-core ECC | m | 70
1 | 7 | 20 | 5 | 10mm² x 4-core ECC | m | 20
1 | 7 | 20 | 6 | 6mm² x 4-core ECC | m | 36
1 | 7 | 20 | 7 | 2.5mm² x 4-core ECC | m | 70
1 | 7 | 20 | 8 | 2.5mm² x 3-core surflex | m | 1620
1 | 7 | 20 |  | LT CABLE TERMINATIONS | H3 | 0
1 | 7 | 20 |  | Termination for 600/1000 volt PVC/PVC/SWA/PVC copper cables. | H4 | 0
1 | 7 | 20 | 9 | 240mm² x 4-core ECC | No | 4
1 | 7 | 21 | 10 | 50mm² x 4-core ECC | No | 2
1 | 7 | 21 | 11 | 16mm² x 4-core ECC | No | 6
1 | 7 | 21 | 12 | 10mm² x 4-core ECC | No | 2
1 | 7 | 21 | 13 | 6mm² x 4-core ECC | No | 4
1 | 7 | 21 | 14 | 2.5mm² x 4-core ECC | No | 4
1 | 7 | 21 | 15 | 2.5mm² x 3-core ECC | No | 29
1 | 7 | 21 |  | EARTH WIRES | H3 | 0
1 | 7 | 21 |  | Bare copper earth conductors strapped to cables | H4 | 0
1 | 7 | 21 | 16 | 240mm² conductor | m | 30
1 | 7 | 21 | 17 | 50mm² conductor | m | 35
1 | 7 | 21 | 18 | 16mm² conductor | m | 70
1 | 7 | 21 | 19 | 6mm² conductor | m | 20
1 | 7 | 21 | 20 | 2.5mm² conductor | m | 1620
1 | 7 | 21 |  | EARTH WIRE TERMINATIONS | H3 | 0
1 | 7 | 21 |  | Bare copper earth conductor terminations includings lugs etc: | H4 | 0
1 | 7 | 21 | 21 | 240mm² conductor | No | 4
1 | 7 | 21 | 22 | 50mm² conductor | No | 2
1 | 7 | 21 | 23 | 16mm² conductor | No | 6
1 | 7 | 21 | 24 | 6mm² conductor | No | 2
1 | 7 | 21 | 25 | 2.5mm² conductor | No | 6
1 | 7 | 22 |  | SUNDRIES | H4 | 0
1 | 7 | 22 | 26 | Test and commission the complete reticulation installation | Item | 1
1 | 7 | 22 | 27 | Issue Electrical Consultant with As-Builts" dwg. for all cables" | Item | 1
1 | 7 | 22 |  | ELECTRICAL DISTRIBUTION BOARDS | H3 | 0
1 | 7 | 22 |  | DISTRIBUTION BOARDS | H4 | 0
1 | 7 | 22 |  | Distribution boards complete with sheet metal tray, frames, sub frames, bus bars, contactors, time switches, switches, 50% provision for future circuit breakers and a typed legend card as shown on the wiring schedules. |  | 0
1 | 7 | 22 | 28 | DB-A1 : Semi Resecced board with lockable doors | No | 1
1 | 7 | 22 |  | Equipment: DB-A1 NORMAL SECTION | H3 | 0
1 | 7 | 22 | 29 | 400 Amp triple pole on load isolator | No | 1
1 | 7 | 22 | 30 | 125 Amp triple pole 15 kA circuit breaker Curve 1 | No | 1
1 | 7 | 22 | 31 | 80 Amp triple pole 6 kA circuit breaker Curve 1 | No | 1
1 | 7 | 22 | 32 | 60 Amp triple pole 6 kA circuit breaker Curve 1 | No | 2
1 | 7 | 22 | 33 | 10 Amp triple pole 6 kA circuit breaker Curve 1 | No | 3
1 | 7 | 22 | 34 | 20 Amp single pole 6 kA circuit breaker Curve 1 | No | 23
1 | 7 | 22 | 35 | Class II Lightning Arrestors with fault indication | No | 4
1 | 7 | 22 | 36 | DB-A2 : Semi Resecced board with lockable doors | No | 1
1 | 7 | 22 |  | Equipment: DB-A2 NORMAL SECTION | H3 | 0
1 | 7 | 22 | 37 | 60 Amp triple pole on load isolator | No | 1
1 | 7 | 23 | 38 | 60 Amp triple pole 6 kA circuit breaker Curve 1 | No | 1
1 | 7 | 23 | 39 | 20 Amp single pole 6 kA circuit breaker Curve 1 | No | 5
1 | 7 | 23 | 40 | Class II Lightning Arrestors with fault indication | No | 4
1 | 7 | 23 |  | Drawings | H3 | 0
1 | 7 | 23 |  | Submit to the Consulting Engineer three (3) sets of the Manufacturer's drawings each for approval of the following distribution boards complete: | H4 | 0
1 | 7 | 23 | 41 | DB. A1 | No | 1
1 | 7 | 23 | 42 | DB. A2 | No | 1
1 | 7 | 23 |  | LIGHTING AND SMALL POWER | H2 | 0
1 | 7 | 23 |  | ISOLATORS | H3 | 0
1 | 7 | 23 |  | Isolator outlets complete with cover plate fixed in flush box or surface mounted. | H4 | 0
1 | 7 | 23 | 43 | 30A double pole + earth mounted weatherproof isolator | No | 28
1 | 7 | 23 |  | CABLE TRAY | H3 | 0
1 | 7 | 23 |  | Galvanised cable tray mounted in ceiling voids or fixed surface against concrete floors/walls | H4 | 0
1 | 7 | 23 |  | The rates for cable tray shall include for hangers, splices, jointing, drilling, etc | H4 | 0
1 | 7 | 23 | 44 | 300mm wire mesh | m | 20
1 | 7 | 23 |  | Extra over 300mm wire mesh accessories | H4 | 0
1 | 7 | 23 | 45 | External bends | No | 2
1 | 7 | 23 | 46 | 90 Degree bends | No | 1
1 | 7 | 24 | 47 | "T joints" | No | 1
1 | 7 | 25 |  | SUNDRIES | H3 | 0
1 | 7 | 25 |  | Provide a Certificate of Compliance by an Accredited person for each of the following: | H4 | 0
1 | 7 | 25 | 48 | DB A1 | No | 1
1 | 7 | 25 | 49 | DB A2 | No | 1
1 | 7 | 25 |  | CIRCUIT LABELLING & TESTING | H3 | 0
1 | 7 | 25 |  | Allow for circuit labelling, testing, balancing and commissioning of the complete electrical installations in the following areas: | H4 | 0
1 | 7 | 25 | 50 | DB A1 | No | 1
1 | 7 | 25 | 51 | DB A2 | No | 1
1 | 7 |  |  |  |  | 0
1 | 8 | 27 | 1 | PRELIMINARIES AND GENERAL ITEMS | Page | 1 | 0
1 | 8 | 27 | 2 | CHILLER PLANTS AND AIR HANDLING UNITS | Page | 4 | 0
1 | 8 | 27 | 3 | CONTROLS | Page | 7 | 0
1 | 8 | 27 | 4 | CHILLED WATER PIPES | Page | 13 | 0
1 | 8 | 27 | 5 | DUCTING | Page | 18 | 0
1 | 8 | 27 | 6 | BUILDERS WORK | Page | 19 | 0
1 | 8 | 27 | 7 | ELECTRICAL POWER SUPPLY | Page | 26 | 0
2 | 1 | 28 | 1 | HVAC INSTALLATION COMPETE WITH ELECTRICAL POWER | Page | 27 | 0
2 | 1 | 28 |  | Sub-total | ST | 0 |  | Sub Total
2 | 1 | 28 |  | Add: Contingencies @ 5% | TAX | 5
2 | 1 | 28 |  | Sub-total | ST | 0 |  | Sub Total
2 | 1 | 28 |  | Add: Value Added Tax (VAT) @ 15% | TAX | 15